## Health Risk
Assessment | Index.index_name | Assessment.index.index_Component.health_component_name | Index.index_Component.health_test_name | Assessment.index.index_Component.measure.gas_measure | Assessment.index.index_Component.measure.measure_name | Assessment.index.index_Component.measure.observation | Assessment.index.index_Component.measure.measure_value
| Health | DGA |  | H PPM
CO2 PPM
CH4 PPM
C2H6 PPM
C2H4 PPM
2FAL Furans PPB
CO PPM
C2H2 PPM
|  | Power Factor and Excitation Current Tests |  |  | Power Factor | 'Power factor results normal. (Good – G)'
'Power factor results show minor degradation. (Deteriorated – D)'
'Power factor results show significant deterioration. (Investigate – I)'
'Power factor results show severe degradation. (Bad – B)'
[5 empty] | Excitation Current | 'Minor deviation in excitation current values and patterns compared to other phases and prior tests'
'Significant deviation in current values and patterns compared to other phases and prior tests.'
'Severe deviation in current values and patterns compared to other phases and prior tests.'
'Normal excitation current values and patterns compared to other phases and prior tests.'
|  | Operation and Maintenance History |  |  |  | 'Operation and Maintenance are normal.'
'Some abnormal operating conditions experienced and/or additional maintenance above normal occurring.'
'Significant operation outside normal and/or significant additional maintenance is required; or forced outage occurs; or outages are regularly extended due to maintenance problems; or similar units are problematic.'
'Repeated forced outages; maintenance not cost effective; or major oil leaks and/or severe mechanical problems; or similar units have failed.'
|  | Age |  |  |  |  | {NUMBER}
|  |  | Turns Ratio Test |  | 'Last Assessment Diff' |  | {DECIMAL}
[5 empty] | 'Nameplate Diff' |  | {DECIMAL}
|  |  | Short Circuit Impedance Test |  |  | 'Less than 1% difference from nameplate impedance'
'1% to 3% difference from nameplate impedance (minor degradation)'
'3% to 5% difference from nameplate impedance (significant degradation)'
'Greater than 5% difference from nameplate impedance (severe degradation)'
|  |  | Core-to-Ground Resistance (Megger) |  |  | 'Greater than 1,000 megohms (results normal)'
'600 to 900 megohms'
'200 to 500 megohms'
'Less than 200 megohms'
|  |  | Winding DC Resistance Measurement |  |  | 'No more than 5% difference between phases or from factory tests'
'5% to 7% difference between phases or from factory tests'
'7% to 10% difference between phases or from factory tests'
'More than 10% difference between phases or from factory tests'
|  |  | Ultrasonic and Sonic Fault Detection |  |  | 'No more than 5% difference between phases or from factory tests'
'5% to 7% difference between phases or from actory tests'
'7% to 10% difference between phases or from factory tests'
'More than 10% difference between phases or from factory tests'
|  |  | Frequency Response Analysis |  |  | 'No deviation compared to prior tests'
'Minor deviation compared to prior tests'
'Moderate deviation compared to prior tests'
'Significant deviation compared to prior tests'
'Severe deviation compared to prior tests'
|  |  | Internal Inspection |  |  | 'Conditions normal'
'Minimal degradation'
'Moderate degradation'
'Severe degradation'
|  |  | Degree of Polymerization |  |  | '900 or higher (no polymerization decrease; results normal)'
'800-700 (minimal polymerization decrease)'
'600-300 (moderate polymerization decrease)'
'<200 (severe polymerization decrease—insulation has no mechanical strength; end of life)'

## Criticality
Assessment | Index.index_name | Index.index_Component.criticality_component_name | Index.index_Component.measure.measure_name | Index.index_Component.measure.observation
| Criticality | Environmental Impact | Air emissions | 'None'
'Non-reportable'
'Reportable'
|  |  | Chemical spills | 'None'
'Non-reportable'
'Reportable'
|  |  | Solid and Hazardous Waste | 'None'
'Non-reportable'
'Reportable'
|  |  | Water and Process Water Impacts | 'None'
'Non-reportable'
'Reportable'
|  | Generation Impact | Capacity Impact | 'None'
'Ten % Reduction'
'Twenty % Reduction'
'Fifty % Reduction or Min Load'
'Hundred % Reduction'
|  |  | Downtime Impact | 'None'
'Low Impact (Down Time < 2 Hours)'
'Medium Impact (Down Time => 2 Hours < 24 Hours)'
'High Impact (Down Time 24 Hours)'
|  |  | Equpment Utilization | 'None'
'Rarely Used'
'Equipment is used < 25 % of the Time'
'Equipment is used > 25 % and < 70 % of the Time'
'Equipment is required to run 70 % up to 100 % of the Time'
|  |  | Frequency of Failure | 'Has not failed or no history of a failure'
'Low – Every 5 Years'
'Moderate – Once every 2 years'
'High - < = 1 year'
|  |  | Equipment Redundancy | 'None'
'In Line Spare Automatic Switch Over'
'In Line Spare Manual Switch Over'
'Desired Capacity Impacted'
'Work Around Available'
|  | Maintenance Impact | Maintenance schedule compliance | 'None'
'Low Impact – Anytime Work'
'Medium Low Impact – Repair within 2 weeks'
'High Impact – Repair within 7 days'
'Urgent Impact – Repair within 48 hours'
'Emergency – Repair within 24 hours'
|  |  | Repair costs | 'None'
'Minimal Impact ($0 - $1000)'
'Low Impact ($1000 - < $10k)'
'Medium ($10k - < $50k)'
'Moderate Impact ($50k - $100k)'
'High Impact (> $100K)'
|  |  | Mean time to repair | 'None'
'Minor 0-30 minutes'
'Moderate 30-120 Minutes'
'Significant 2-8 Hours'
'Major 8-24 hours'
'Severe >24 hours'
|  | Safety Impact | Injury from failure | 'None'
'Minor Injury (First Aid/Minor Medical Aid)'
'Major Injury (Lost Time)'
'Fatality or Permanent Disability'
|  |  | Injury during repair | 'None'
'Low Risk (First Aid/Minor Medical Aid)'
'Medium Risk (Rigging, Fall Arrest, Confined Space)'
'High Risk (Critical Lift, Permit Required Confined Space)'
|  | Spares availability |  | 'Complete unit replacement on site'
'Partial unit replacement on site'
'Parts available within 7 days'
'Parts available > 7 to 30 days'
'Parts available > 30 days or none identified'