## Health Risk
Assessment | Assesment.index.index_name | Assessment.index.index_Component.health_component_name | Assesment.index.index_Component.health_test_name | Assessment.index.index_Component.measure.gas_measure | Assessment.index.index_Component.measure.measure_name | Assessment.index.index_Component.measure.observation | Assessment.index.index_Component.measure.measure_value
| Health | DGA |  | H PPM
CO2 PPM
CH4 PPM
C2H6 PPM
C2H4 PPM
2FAL Furans PPB
CO PPM
C2H2 PPM
|  | Power Factor and Excitation Current Tests |  |  | Power Factor | 'Power factor results normal. (Good – G)'
'Power factor results show minor degradation. (Deteriorated – D)'
'Power factor results show significant deterioration. (Investigate – I)'
'Power factor results show severe degradation. (Bad – B)'
[5 empty] | Excitation Current | 'Minor deviation in excitation current values and patterns compared to other phases and prior tests'
'Significant deviation in current values and patterns compared to other phases and prior tests.'
'Severe deviation in current values and patterns compared to other phases and prior tests.'
'Normal excitation current values and patterns compared to other phases and prior tests.'
|  | Operation and Maintenance History |  |  |  | 'Operation and Maintenance are normal.'
'Some abnormal operating conditions experienced and/or additional maintenance above normal occurring.'
'Significant operation outside normal and/or significant additional maintenance is required; or forced outage occurs; or outages are regularly extended due to maintenance problems; or similar units are problematic.'
'Repeated forced outages; maintenance not cost effective; or major oil leaks and/or severe mechanical problems; or similar units have failed.'
|  | Age |  |  |  |  | {NUMBER}
|  |  | Turns Ratio Test |  | 'Last Assessment Diff' |  | {DECIMAL}
[5 empty] | 'Nameplate Diff' |  | {DECIMAL}
|  |  | Short Circuit Impedance Test |  |  | 'Less than 1% difference from nameplate impedance'
'1% to 3% difference from nameplate impedance (minor degradation)'
'3% to 5% difference from nameplate impedance (significant degradation)'
'Greater than 5% difference from nameplate impedance (severe degradation)'
|  |  | Core-to-Ground Resistance (Megger) |  |  | 'Greater than 1,000 megohms (results normal)'
'600 to 900 megohms'
'200 to 500 megohms'
'Less than 200 megohms'
|  |  | Winding DC Resistance Measurement |  |  | 'No more than 5% difference between phases or from factory tests'
'5% to 7% difference between phases or from factory tests'
'7% to 10% difference between phases or from factory tests'
'More than 10% difference between phases or from factory tests'
|  |  | Ultrasonic and Sonic Fault Detection |  |  | 'No more than 5% difference between phases or from factory tests'
'5% to 7% difference between phases or from actory tests'
'7% to 10% difference between phases or from factory tests'
'More than 10% difference between phases or from factory tests'
|  |  | Frequency Response Analysis |  |  | 'No deviation compared to prior tests'
'Minor deviation compared to prior tests'
'Moderate deviation compared to prior tests'
'Significant deviation compared to prior tests'
'Severe deviation compared to prior tests'
|  |  | Internal Inspection |  |  | 'Conditions normal'
'Minimal degradation'
'Moderate degradation'
'Severe degradation'
|  |  | Degree of Polymerization |  |  | '900 or higher (no polymerization decrease; results normal)'
'800-700 (minimal polymerization decrease)'
'600-300 (moderate polymerization decrease)'
'<200 (severe polymerization decrease—insulation has no mechanical strength; end of life)'

## Criticality
Assessment | Assesment.index.index_name | Assesment.index.index_Component.criticality_component_name | Assesment.index.index_Component.measure.measure_name | Assesment.index.index_Component.measure.observation
| Criticality | Environmental Impact | Air emissions | None
Non-reportable
Reportable
|  |  | Chemical spills | None
Non-reportable
Reportable
|  |  | Solid and Hazardous Waste | None
Non-reportable
Reportable
|  |  | Water and Process Water Impacts | None
Non-reportable
Reportable
|  | Generation Impact | Capacity Impact | None
Ten % Reduction
Twenty % Reduction
Fifty % Reduction or Min Load
Hundred % Reduction
|  |  | Downtime Impact | None
Low Impact (Down Time < 2 Hours)
Medium Impact (Down Time => 2 Hours < 24 Hours)
High Impact (Down Time 24 Hours)
|  |  | Equpment Utilization | None
Rarely Used
Equipment is used < 25 % of the Time
Equipment is used > 25 % and < 70 % of the Time
Equipment is required to run 70 % up to 100 % of the Time
|  |  | Frequency of Failure | Has not failed or no history of a failure
Low – Every 5 Years
Moderate – Once every 2 years
High - < = 1 year
|  |  | Equipment Redundancy | None
In Line Spare Automatic Switch Over
In Line Spare Manual Switch Over
Desired Capacity Impacted
Work Around Available
|  | Maintenance Impact | Maintenance schedule compliance | None
Low Impact – Anytime Work
Medium Low Impact – Repair within 2 weeks
High Impact – Repair within 7 days
Urgent Impact – Repair within 48 hours
Emergency – Repair within 24 hours
|  |  | Repair costs | None
Minimal Impact ($0 - $1000)
Low Impact ($1000 - < $10k)
Medium ($10k - < $50k)
Moderate Impact ($50k - $100k)
High Impact (> $100K)
|  |  | Mean time to repair | None
Minor 0-30 minutes
Moderate 30-120 Minutes
Significant 2-8 Hours
Major 8-24 hours
Severe >24 hours
|  | Safety Impact | Injury from failure | None
Minor Injury (First Aid/Minor Medical Aid)
Major Injury (Lost Time)
Fatality or Permanent Disability
|  |  | Injury during repair | None
Low Risk (First Aid/Minor Medical Aid)
Medium Risk (Rigging, Fall Arrest, Confined Space)
High Risk (Critical Lift, Permit Required Confined Space)
|  | Spares availability |  | Complete unit replacement on site
Partial unit replacement on site
Parts available within 7 days
Parts available > 7 to 30 days
Parts available > 30 days or none identified